## Time instant calculation
Start date | 2021-01-21
End date | 2021-01-21
Start time instant | 1814400 | 21
End time instant | 1900800 | 22
Start date | 2021-07-15 |  | SummerDesignDay
End date | 2021-08-15
Start time instant | 16934400 | 196 | 282240
End time instant | 19699200 | 228 | 328320 | 46081
Start date | 2021-10-21
End date | 2021-10-21
Start time instant | 25401600 | 294
End time instant | 25488000 | 295
Start date | 2021-12-25 |  | WinterDesignDay
End date | 2021-12-28
Start time instant | 31017600 | 359 | 516960
End time instant | 31363200 | 363 | 522720 | 5761
Start date | 2021-01-05
End date | 2021-01-08
Start time instant | 432000 | 5
End time instant | 777600 | 9
Start date | 2021-01-02
End date | 2021-01-03
Start time instant | 172800 | 2
End time instant | 345600 | 4

## Internal gains
Lighting intensity | 10.764 | W/m2
Total area | 1660.74 | m2
Total lighting load | 17876.2054 | W
People density | 18.58 | m2/person
Total number of people | 89.3832 | persons
Heat gain rate (IP) per person | 400 | BTU/h
Heat gain rate (SI) per person | 117.24 | W
Total people load | 10479.2873 | W
Electric equipment load | 13402.0174 | W
Total internal heat gain | 41757.51 | W
Internal heat gain/m2 | 25.1439 | W/m2

## Coil sizing table
| Coil Type | Coil Location | HVAC Type | HVAC Name | Zone Name(s) | System Sizing Method Concurrence | System Sizing Method Capacity | System Sizing Method Air Flow | Autosized Coil Capacity? | Autosized Coil Airflow? | Autosized Coil Water Flow? | OA Pretreated prior to coil inlet? | Coil Final Gross Total Capacity [W] | Coil Final Gross Sensible Capacity [W] | Coil Final Reference Air Volume Flow Rate [m3/s] | Coil Final Reference Plant Fluid Volume Flow Rate [m3/s] | Coil U-value Times Area Value [W/K] | Terminal Unit Reheat Coil Multiplier | DX Coil Capacity Increase Ratio from Too Low Flow/Capacity Ratio | DX Coil Capacity Decrease Ratio from Too High Flow/Capacity Ratio | Moist Air Heat Capacity [J/kg-K] | Dry Air Heat Capacity [J/kg-K] | Standard Air Density Adjusted for Elevation [kg/m3] | Supply Fan Name for Coil | Supply Fan Type for Coil | Supply Fan Maximum Air Volume Flow Rate [m3/s] | Supply Fan Maximum Air Mass Flow Rate [kg/s] | Plant Name for Coil | Plant Fluid Specific Heat Capacity [J/kg-K] | Plant Fluid Density [kg/m3] | Plant Maximum Fluid Mass Flow Rate [kg/s] | Plant Design Fluid Return Temperature [C] | Plant Design Fluid Supply Temperature [C] | Plant Design Fluid Temperature Difference [deltaC] | Plant Design Capacity [W] | Coil Capacity Percentage of Plant Design Capacity [%] | Coil Fluid Flow Rate Percentage of Plant Design Flow Rate [%] | Design Day Name at Sensible Ideal Loads Peak | Date/Time at Sensible Ideal Loads Peak | Design Day Name at Total Ideal Loads Peak | Date/Time at Total Ideal Loads Peak | Design Day Name at Air Flow Ideal Loads Peak | Date/Time at Air Flow Ideal Loads Peak | Coil Total Capacity at Ideal Loads Peak [W] | Coil Sensible Capacity at Ideal Loads Peak [W] | Coil Off-Rating Capacity Modifier at Ideal Loads Peak [ ] | Coil Air Mass Flow Rate at Ideal Loads Peak [kg/s] | Coil Air Volume Flow Rate at Ideal Loads Peak [m3/s] | Coil Entering Air Drybulb at Ideal Loads Peak [C] | Coil Entering Air Wetbulb at Ideal Loads Peak [C] | Coil Entering Air Humidity Ratio at Ideal Loads Peak [KGWATER/KGDRYAIR] | Coil Entering Air Enthalpy at Ideal Loads Peak [J/KG-K] | Coil Leaving Air Drybulb at Ideal Loads Peak [C] | Coil Leaving Air Wetbulb at Ideal Loads Peak [C] | Coil Leaving Air Humidity Ratio at Ideal Loads Peak [C] | Coil Leaving Air Enthalpy at Ideal Loads Peak [J/KG-K] | Coil Plant Fluid Mass Flow Rate at Ideal Loads Peak [kg/s] | Coil Entering Plant Fluid Temperature at Ideal Loads Peak [C] | Coil Leaving Plant Fluid Temperature at Ideal Loads Peak [C] | Coil Plant Fluid Temperature Difference at Ideal Loads Peak [deltaC] | Supply Fan Air Heat Gain at Ideal Loads Peak [W] | Coil and Fan Net Total Capacity at Ideal Loads Peak [W] | Outdoor Air Drybulb at Ideal Loads Peak [C] | Outdoor Air Humidity Ratio at Ideal Loads Peak [KGWATER/KGDRYAIR] | Outdoor Air Wetbulb at Ideal Loads Peak [C] | Outdoor Air Volume Flow Rate at Ideal Loads Peak [m3/s] | Outdoor Air Flow Percentage at Ideal Loads Peak [%] | System Return Air Drybulb at Ideal Loads Peak [C] | System Return Air Humidity Ratio at Ideal Loads Peak [KGWATER/KGDRYAIR] | Zone Air Drybulb at Ideal Loads Peak [C] | Zone Air Humidity Ratio at Ideal Loads Peak [KGWATER/KGDRYAIR] | Zone Air Relative Humidity at Ideal Loads Peak [%] | Zone Sensible Heat Gain at Ideal Loads Peak [W] | Zone Latent Heat Gain at Ideal Loads Peak [W] | Coil Total Capacity at Rating Conditions [W] | Coil Sensible Capacity at Rating Conditions [W] | Coil Air Mass Flow Rate at Rating Conditions [kg/s] | Coil Entering Air Drybulb at Rating Conditions [C] | Coil Entering Air Wetbulb at Rating Conditions [C] | Coil Entering Air Humidity Ratio at Rating Conditions [KGWATER/KGDRYAIR] | Coil Entering Air Enthalpy at Rating Conditions [J/KG-K] | Coil Leaving Air Drybulb at Rating Conditions [C] | Coil Leaving Air Wetbulb at Rating Conditions [C] | Coil Leaving Air Humidity Ratio at Rating Conditions [KGWATER/KGDRYAIR] | Coil Leaving Air Enthalpy at Rating Conditions [J/KG-K]
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Electric | Zone Equipment | ZONEHVAC:AIRDISTRIBUTIONUNIT | CORE_BOTTOM VAV BOX | CORE_BOTTOM | N/A | N/A | N/A | Yes | No | unknown | No | 21843.702 | 21843.702 | -999 | -999 | -999 | -999 | 1 | 1 | 1019.7116 | 1004.8586 | 1.185 | unknown | unknown | -999 | -999 |  | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | WINTERDESIGNDAY | unknown | unknown | unknown | WINTERDESIGNDAY | unknown | 21843.7 | 13957.79 | 1 | 0.50323 | 0.42467 | 12.8 | 11.45 | 0.008 | 33059.8 | 40 | 20.96 | 0.008 | 60796 | -999 | -999 | -999 | -999 | 0 | 21843.7 | -8 | 0.0016173 | -8.57 | 0 | 0 | 21 | 0.008 | 21 | 0.008 | 50.8949 | 0 | 0 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Electric | Zone Equipment | ZONEHVAC:AIRDISTRIBUTIONUNIT | CORE_MID VAV BOX | CORE_MID | N/A | N/A | N/A | Yes | No | unknown | No | 14579.559 | 14579.559 | -999 | -999 | -999 | -999 | 1 | 1 | 1019.7116 | 1004.8586 | 1.185 | unknown | unknown | -999 | -999 |  | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | WINTERDESIGNDAY | unknown | unknown | unknown | WINTERDESIGNDAY | unknown | 14579.56 | 13957.79 | 1 | 0.50323 | 0.42467 | 12.8 | 11.45 | 0.008 | 33059.8 | 40 | 20.96 | 0.008 | 60796 | -999 | -999 | -999 | -999 | 0 | 14579.56 | -2 | 0.0027382 | -2.76 | 0 | 0 | 20.88 | 0.011993 | 21 | 0.011993 | 75.8107 | 5269.1 | 0 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Electric | Zone Equipment | ZONEHVAC:AIRDISTRIBUTIONUNIT | CORE_TOP VAV BOX | CORE_TOP | N/A | N/A | N/A | Yes | No | unknown | No | 39882.612 | 39882.612 | -999 | -999 | -999 | -999 | 1 | 1 | 1019.7116 | 1004.8586 | 1.185 | unknown | unknown | -999 | -999 |  | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | WINTERDESIGNDAY | unknown | unknown | unknown | WINTERDESIGNDAY | unknown | 39882.61 | 39882.61 | 1 | 1.4379 | 1.2134 | 12.8 | 11.45 | 0.008 | 33059.8 | 40 | 20.96 | 0.008 | 60796 | -999 | -999 | -999 | -999 | 0 | 39882.61 | -2 | 0.0027382 | -2.76 | 0 | 0 | 20.57 | 0.009487 | 21 | 0.009487 | 60.1972 | 29063.36 | 0 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Electric | Zone Equipment | ZONEHVAC:AIRDISTRIBUTIONUNIT | PERIMETER_TOP_ZN_3 VAV BOX | PERIMETER_TOP_ZN_3 | N/A | N/A | N/A | Yes | No | unknown | No | 16708.18 | 16708.18 | -999 | -999 | -999 | -999 | 1 | 1 | 1019.7116 | 1004.8586 | 1.185 | unknown | unknown | -999 | -999 |  | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | WINTERDESIGNDAY | unknown | unknown | unknown | WINTERDESIGNDAY | unknown | 16708.18 | 16708.18 | 1 | 0.6024 | 0.50835 | 12.8 | 11.45 | 0.008 | 33059.8 | 40 | 20.96 | 0.008 | 60796 | -999 | -999 | -999 | -999 | 0 | 16708.18 | -2 | 0.0027382 | -2.76 | 0 | 0 | 20.67 | 0.0075953 | 21 | 0.0075953 | 48.3581 | 12104.37 | 0 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Electric | Zone Equipment | ZONEHVAC:AIRDISTRIBUTIONUNIT | PERIMETER_TOP_ZN_2 VAV BOX | PERIMETER_TOP_ZN_2 | N/A | N/A | N/A | Yes | No | unknown | No | 11032.4 | 11032.4 | -999 | -999 | -999 | -999 | 1 | 1 | 1019.7116 | 1004.8586 | 1.185 | unknown | unknown | -999 | -999 |  | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | WINTERDESIGNDAY | unknown | unknown | unknown | WINTERDESIGNDAY | unknown | 11032.4 | 11032.4 | 1 | 0.39776 | 0.33566 | 12.8 | 11.45 | 0.008 | 33059.8 | 40 | 20.96 | 0.008 | 60796 | -999 | -999 | -999 | -999 | 0 | 11032.4 | -2 | 0.0027382 | -2.76 | 0 | 0 | 20.67 | 0.0076145 | 21 | 0.0076145 | 48.4782 | 7982.2 | 0 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Electric | Zone Equipment | ZONEHVAC:AIRDISTRIBUTIONUNIT | PERIMETER_TOP_ZN_1 VAV BOX | PERIMETER_TOP_ZN_1 | N/A | N/A | N/A | Yes | No | unknown | No | 16782.888 | 16782.888 | -999 | -999 | -999 | -999 | 1 | 1 | 1019.7116 | 1004.8586 | 1.185 | unknown | unknown | -999 | -999 |  | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | WINTERDESIGNDAY | unknown | unknown | unknown | WINTERDESIGNDAY | unknown | 16782.89 | 16782.89 | 1 | 0.60509 | 0.51062 | 12.8 | 11.45 | 0.008 | 33059.8 | 40 | 20.96 | 0.008 | 60796 | -999 | -999 | -999 | -999 | 0 | 16782.89 | -2 | 0.0027382 | -2.76 | 0 | 0 | 20.67 | 0.0075892 | 21 | 0.0075892 | 48.3198 | 12157.58 | 0 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Electric | Zone Equipment | ZONEHVAC:AIRDISTRIBUTIONUNIT | PERIMETER_TOP_ZN_4 VAV BOX | PERIMETER_TOP_ZN_4 | N/A | N/A | N/A | Yes | No | unknown | No | 10969.522 | 10969.522 | -999 | -999 | -999 | -999 | 1 | 1 | 1019.7116 | 1004.8586 | 1.185 | unknown | unknown | -999 | -999 |  | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | WINTERDESIGNDAY | unknown | unknown | unknown | WINTERDESIGNDAY | unknown | 10969.52 | 10969.52 | 1 | 0.3955 | 0.33375 | 12.8 | 11.45 | 0.008 | 33059.8 | 40 | 20.96 | 0.008 | 60796 | -999 | -999 | -999 | -999 | 0 | 10969.52 | -2 | 0.0027382 | -2.76 | 0 | 0 | 20.67 | 0.007611 | 21 | 0.007611 | 48.4564 | 7938.14 | 0 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Electric | Zone Equipment | ZONEHVAC:AIRDISTRIBUTIONUNIT | PERIMETER_BOT_ZN_3 VAV BOX | PERIMETER_BOT_ZN_3 | N/A | N/A | N/A | Yes | No | unknown | No | 7862.045 | 7862.045 | -999 | -999 | -999 | -999 | 1 | 1 | 1019.7116 | 1004.8586 | 1.185 | unknown | unknown | -999 | -999 |  | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | WINTERDESIGNDAY | unknown | unknown | unknown | WINTERDESIGNDAY | unknown | 7862.04 | 7862.04 | 1 | 0.28346 | 0.2392 | 12.8 | 11.45 | 0.008 | 33059.8 | 40 | 20.96 | 0.008 | 60796 | -999 | -999 | -999 | -999 | 0 | 7862.04 | -2 | 0.0027382 | -2.76 | 0 | 0 | 20.75 | 0.0059786 | 20.99 | 0.0059786 | 38.1696 | 5663.89 | 0 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Electric | Zone Equipment | ZONEHVAC:AIRDISTRIBUTIONUNIT | PERIMETER_BOT_ZN_2 VAV BOX | PERIMETER_BOT_ZN_2 | N/A | N/A | N/A | Yes | No | unknown | No | 5456.853 | 5456.853 | -999 | -999 | -999 | -999 | 1 | 1 | 1019.7116 | 1004.8586 | 1.185 | unknown | unknown | -999 | -999 |  | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | WINTERDESIGNDAY | unknown | unknown | unknown | WINTERDESIGNDAY | unknown | 5456.85 | 5456.85 | 1 | 0.19674 | 0.16602 | 12.8 | 11.45 | 0.008 | 33059.8 | 40 | 20.96 | 0.008 | 60796 | -999 | -999 | -999 | -999 | 0 | 5456.85 | -2 | 0.0027382 | -2.76 | 0 | 0 | 20.73 | 0.0061326 | 20.99 | 0.0061326 | 39.1438 | 3933.85 | 0 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Electric | Zone Equipment | ZONEHVAC:AIRDISTRIBUTIONUNIT | PERIMETER_BOT_ZN_1 VAV BOX | PERIMETER_BOT_ZN_1 | N/A | N/A | N/A | Yes | No | unknown | No | 33259.285 | 33259.285 | -999 | -999 | -999 | -999 | 1 | 1 | 1019.7116 | 1004.8586 | 1.185 | unknown | unknown | -999 | -999 |  | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | WINTERDESIGNDAY | unknown | unknown | unknown | WINTERDESIGNDAY | unknown | 33259.29 | 33259.29 | 1 | 1.1991 | 1.0119 | 12.8 | 11.45 | 0.008 | 33059.8 | 40 | 20.96 | 0.008 | 60796 | -999 | -999 | -999 | -999 | 0 | 33259.29 | -5 | 0.0022577 | -5.42 | 0 | 0 | 20.98 | 0.0056318 | 20.98 | 0.0056318 | 36.0188 | 23257.08 | 0 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Electric | Zone Equipment | ZONEHVAC:AIRDISTRIBUTIONUNIT | PERIMETER_BOT_ZN_4 VAV BOX | PERIMETER_BOT_ZN_4 | N/A | N/A | N/A | Yes | No | unknown | No | 6167.828 | 6167.828 | -999 | -999 | -999 | -999 | 1 | 1 | 1019.7116 | 1004.8586 | 1.185 | unknown | unknown | -999 | -999 |  | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | WINTERDESIGNDAY | unknown | unknown | unknown | WINTERDESIGNDAY | unknown | 6167.83 | 5359.08 | 1 | 0.19322 | 0.16305 | 12.8 | 11.45 | 0.008 | 33059.8 | 40 | 20.96 | 0.008 | 60796 | -999 | -999 | -999 | -999 | 0 | 6167.83 | -2 | 0.0027382 | -2.76 | 0 | 0 | 20.74 | 0.0061023 | 20.99 | 0.0061023 | 38.9522 | 3862.29 | 0 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Electric | Zone Equipment | ZONEHVAC:AIRDISTRIBUTIONUNIT | PERIMETER_MID_ZN_3 VAV BOX | PERIMETER_MID_ZN_3 | N/A | N/A | N/A | Yes | No | unknown | No | 10659.162 | 10659.162 | -999 | -999 | -999 | -999 | 1 | 1 | 1019.7116 | 1004.8586 | 1.185 | unknown | unknown | -999 | -999 |  | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | WINTERDESIGNDAY | unknown | unknown | unknown | WINTERDESIGNDAY | unknown | 10659.16 | 10659.16 | 1 | 0.38431 | 0.3243 | 12.8 | 11.45 | 0.008 | 33059.8 | 40 | 20.96 | 0.008 | 60796 | -999 | -999 | -999 | -999 | 0 | 10659.16 | -2 | 0.0027382 | -2.76 | 0 | 0 | 20.66 | 0.0064675 | 20.99 | 0.0064675 | 41.2593 | 7742.6 | 0 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Electric | Zone Equipment | ZONEHVAC:AIRDISTRIBUTIONUNIT | PERIMETER_MID_ZN_2 VAV BOX | PERIMETER_MID_ZN_2 | N/A | N/A | N/A | Yes | No | unknown | No | 7286.515 | 7286.515 | -999 | -999 | -999 | -999 | 1 | 1 | 1019.7116 | 1004.8586 | 1.185 | unknown | unknown | -999 | -999 |  | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | WINTERDESIGNDAY | unknown | unknown | unknown | WINTERDESIGNDAY | unknown | 7286.51 | 7286.51 | 1 | 0.26271 | 0.22169 | 12.8 | 11.45 | 0.008 | 33059.8 | 40 | 20.96 | 0.008 | 60796 | -999 | -999 | -999 | -999 | 0 | 7286.51 | -2 | 0.0027382 | -2.76 | 0 | 0 | 20.64 | 0.0065906 | 20.99 | 0.0065906 | 42.0365 | 5296.66 | 0 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Electric | Zone Equipment | ZONEHVAC:AIRDISTRIBUTIONUNIT | PERIMETER_MID_ZN_1 VAV BOX | PERIMETER_MID_ZN_1 | N/A | N/A | N/A | Yes | No | unknown | No | 10477.82 | 10477.82 | -999 | -999 | -999 | -999 | 1 | 1 | 1019.7116 | 1004.8586 | 1.185 | unknown | unknown | -999 | -999 |  | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | WINTERDESIGNDAY | unknown | unknown | unknown | WINTERDESIGNDAY | unknown | 10477.82 | 10477.82 | 1 | 0.37777 | 0.31879 | 12.8 | 11.45 | 0.008 | 33059.8 | 40 | 20.96 | 0.008 | 60796 | -999 | -999 | -999 | -999 | 0 | 10477.82 | -2 | 0.0027382 | -2.76 | 0 | 0 | 20.67 | 0.0064388 | 20.99 | 0.0064388 | 41.0779 | 7605.34 | 0 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Electric | Zone Equipment | ZONEHVAC:AIRDISTRIBUTIONUNIT | PERIMETER_MID_ZN_4 VAV BOX | PERIMETER_MID_ZN_4 | N/A | N/A | N/A | Yes | No | unknown | No | 7998.055 | 7998.055 | -999 | -999 | -999 | -999 | 1 | 1 | 1019.7116 | 1004.8586 | 1.185 | unknown | unknown | -999 | -999 |  | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | WINTERDESIGNDAY | unknown | unknown | unknown | WINTERDESIGNDAY | unknown | 7998.05 | 7187.33 | 1 | 0.25913 | 0.21867 | 12.8 | 11.45 | 0.008 | 33059.8 | 40 | 20.96 | 0.008 | 60796 | -999 | -999 | -999 | -999 | 0 | 7998.05 | -2 | 0.0027382 | -2.76 | 0 | 0 | 20.64 | 0.0065691 | 20.99 | 0.0065691 | 41.9008 | 5223.33 | 0 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999
PACU_VAV_BOT_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | AirLoop | AirLoopHVAC | PACU_VAV_BOT | CORE_BOTTOM; PERIMETER_BOT_ZN_3; PERIMETER_BOT_ZN_2; PERIMETER_BOT_ZN_1; PERIMETER_BOT_ZN_4; | Coincident | CoolingDesignCapacity | N/A | Yes | Yes | unknown | No | 98616.316 | 71889.689 | 4.3748 | -999 | -999 | -999 | 1 | 1 | 1021.9127 | 1004.8586 | 1.185 | PACU_VAV_BOT FAN | Fan:VariableVolume | 4.3748 | 5.1842 |  | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | unknown | unknown | unknown | unknown | unknown | unknown | 102577.7 | 92890.61 | 0.9614 | 5.1842 | 4.3748 | 27.76 | 18.06 | 0.009184 | 51337.8 | 10.89 | 10.89 | 0.0085 | 32372.4 | -999 | -999 | -999 | -999 | 10120.515 | 92457.18 | 39 | 0.010259 | 22.26 | 1.0973 | 25.0814 | 24 | 0.0088241 | 24 | 0.0089151 | 47.2019 | 57023.33 | 0 | 101636.42 | 72889.93 | 4.9789 | 26.67 | 19.44 | 0.011179 | 55307.7 | 12.33 | 12.32 | 0.0089152 | 34894.3
PACU_VAV_BOT_HEATC | Coil:Heating:Fuel | AirLoop | AirLoopHVAC | PACU_VAV_BOT | CORE_BOTTOM; PERIMETER_BOT_ZN_3; PERIMETER_BOT_ZN_2; PERIMETER_BOT_ZN_1; PERIMETER_BOT_ZN_4; | Coincident | HeatingDesignCapacity | N/A | Yes | No | unknown | No | 22443.042 | 22443.042 | -999 | -999 | -999 | -999 | 1 | 1 | 1019.7116 | 1004.8586 | 1.185 | PACU_VAV_BOT FAN | Fan:VariableVolume | 4.3748 | 5.1842 |  | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | WINTERDESIGNDAY | unknown | unknown | unknown | unknown | unknown | 22443.04 | 22443.04 | 1 | 1.5552 | 1.3124 | -3.26 | -3.96 | 0.0024691 | 2883.6 | 12.8 | 11.45 | 0.008 | 33059.8 | -999 | -999 | -999 | -999 | 0 | 22443.04 | -4.5 | 0.0024593 | -4.77 | 1.0973 | 83.6046 | 13.43 | 0.0026019 | 20.99 | 0.0062545 | 39.9355 | 13603.54 | 0 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999
PACU_VAV_MID_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | AirLoop | AirLoopHVAC | PACU_VAV_MID | CORE_MID; PERIMETER_MID_ZN_3; PERIMETER_MID_ZN_2; PERIMETER_MID_ZN_1; PERIMETER_MID_ZN_4; | Coincident | CoolingDesignCapacity | N/A | Yes | Yes | unknown | No | 91018.176 | 63556.811 | 3.6684 | -999 | -999 | -999 | 1 | 1 | 1022.9657 | 1004.8586 | 1.185 | PACU_VAV_MID FAN | Fan:VariableVolume | 3.6684 | 4.3471 |  | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | unknown | unknown | unknown | unknown | unknown | unknown | 92862.35 | 78643.67 | 0.9801 | 4.3471 | 3.6684 | 28.67 | 18.8 | 0.0097505 | 53709 | 10.86 | 10.86 | 0.0085 | 32344.5 | -999 | -999 | -999 | -999 | 8616.87 | 84245.48 | 39 | 0.011622 | 23.17 | 1.1411 | 31.1074 | 24 | 0.0089052 | 24 | 0.0088484 | 46.8513 | 49686.65 | 0 | 93805.59 | 64545.31 | 4.1749 | 26.67 | 19.44 | 0.011179 | 55307.7 | 11.52 | 11.49 | 0.008431 | 32839
PACU_VAV_MID_HEATC | Coil:Heating:Fuel | AirLoop | AirLoopHVAC | PACU_VAV_MID | CORE_MID; PERIMETER_MID_ZN_3; PERIMETER_MID_ZN_2; PERIMETER_MID_ZN_1; PERIMETER_MID_ZN_4; | Coincident | HeatingDesignCapacity | N/A | Yes | No | unknown | No | 19394.699 | 19394.699 | -999 | -999 | -999 | -999 | 1 | 1 | 1019.7116 | 1004.8586 | 1.185 | PACU_VAV_MID FAN | Fan:VariableVolume | 3.6684 | 4.3471 |  | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | WINTERDESIGNDAY | unknown | unknown | unknown | unknown | unknown | 19394.7 | 18271.85 | 1 | 1.3041 | 1.1005 | -0.94 | -1.39 | 0.0032372 | 7145.7 | 12.8 | 11.45 | 0.008 | 33059.8 | -999 | -999 | -999 | -999 | 0 | 19394.7 | -2 | 0.0029 | -2.52 | 1.1411 | 103.6915 | 13.73 | 0.0079051 | 21 | 0.0080502 | 51.221 | 23408.55 | 0 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999
PACU_VAV_TOP_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | AirLoop | AirLoopHVAC | PACU_VAV_TOP | CORE_TOP; PERIMETER_TOP_ZN_3; PERIMETER_TOP_ZN_2; PERIMETER_TOP_ZN_1; PERIMETER_TOP_ZN_4; | Coincident | CoolingDesignCapacity | N/A | Yes | Yes | unknown | No | 107840.309 | 78105.871 | 4.7182 | -999 | -999 | -999 | 1 | 1 | 1022.34 | 1004.8586 | 1.185 | PACU_VAV_TOP FAN | Fan:VariableVolume | 4.7182 | 5.5912 |  | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | unknown | unknown | unknown | unknown | unknown | unknown | 111914.73 | 98022.39 | 0.9636 | 5.5912 | 4.7182 | 27.48 | 18.15 | 0.0094139 | 51637.8 | 10.89 | 10.89 | 0.0085 | 32373.2 | -999 | -999 | -999 | -999 | 10915.038 | 100999.69 | 39 | 0.011393 | 23.02 | 1.095 | 23.2075 | 24 | 0.0088158 | 24 | 0.0087863 | 46.5273 | 63902.94 | 0 | 111142.89 | 79173.52 | 5.3698 | 26.67 | 19.44 | 0.011179 | 55307.7 | 12.23 | 12.21 | 0.0088447 | 34609.9
PACU_VAV_TOP_HEATC | Coil:Heating:Fuel | AirLoop | AirLoopHVAC | PACU_VAV_TOP | CORE_TOP; PERIMETER_TOP_ZN_3; PERIMETER_TOP_ZN_2; PERIMETER_TOP_ZN_1; PERIMETER_TOP_ZN_4; | Coincident | HeatingDesignCapacity | N/A | Yes | No | unknown | No | 22687.185 | 22687.185 | -999 | -999 | -999 | -999 | 1 | 1 | 1019.7116 | 1004.8586 | 1.185 | PACU_VAV_TOP FAN | Fan:VariableVolume | 4.7182 | 5.5912 |  | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | WINTERDESIGNDAY | unknown | unknown | unknown | unknown | unknown | 22687.19 | 22687.19 | 1 | 1.6773 | 1.4155 | -7 | -7.32 | 0.0019335 | -2223.5 | 12.8 | 11.45 | 0.008 | 33059.8 | -999 | -999 | -999 | -999 | 0 | 22687.19 | -7 | 0.0019335 | -7.32 | 1.095 | 77.3585 | 21 | 0.010159 | 21 | 0.0083893 | 53.337 | 16379.32 | 0 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999

## Peak sensible cooling
| Calculated Design Load [W] | User Design Load [W] | User Design Load per Area [W/m2] | Calculated Design Air Flow [m3/s] | User Design Air Flow [m3/s] | Design Day Name | Date/Time Of Peak {TIMESTAMP} | Thermostat Setpoint Temperature at Peak Load [C] | Indoor Temperature at Peak Load [C] | Indoor Humidity Ratio at Peak Load [kgWater/kgAir] | Outdoor Temperature at Peak Load [C] | Outdoor Humidity Ratio at Peak Load [kgWater/kgAir] | Minimum Outdoor Air Flow Rate [m3/s] | Heat Gain Rate from DOAS [W]
PERIMETER_TOP_ZN_4 | 12271.21 | 12271.21 | 93.49 | 0.906 | 0.906 | SUMMERDESIGNDAY | 2021-07-28 17:00 | 24 | 24 | 0.00864 | 39 | 0.01162 | 0.057 | 0
PERIMETER_TOP_ZN_3 | 9033.64 | 9033.64 | 43.57 | 0.667 | 0.667 | SUMMERDESIGNDAY | 2021-07-21 15:40 | 24 | 24 | 0.00879 | 37.67 | 0.00993 | 0.09 | 0
PERIMETER_TOP_ZN_2 | 8838.48 | 8838.48 | 67.33 | 0.653 | 0.653 | SUMMERDESIGNDAY | 2021-07-21 09:10 | 24 | 24 | 0.00866 | 27.33 | 0.00729 | 0.057 | 0
PERIMETER_TOP_ZN_1 | 10776.37 | 10776.37 | 51.97 | 0.796 | 0.796 | SUMMERDESIGNDAY | 2021-07-21 14:00 | 24 | 24 | 0.00873 | 36 | 0.00904 | 0.09 | 0
PERIMETER_MID_ZN_4 | 10986.67 | 10986.67 | 83.71 | 0.811 | 0.811 | SUMMERDESIGNDAY | 2021-07-28 17:00 | 24 | 24 | 0.00865 | 39 | 0.01162 | 0.057 | 0
PERIMETER_MID_ZN_3 | 7398.31 | 7398.31 | 35.68 | 0.546 | 0.546 | SUMMERDESIGNDAY | 2021-07-21 15:50 | 24 | 24 | 0.00885 | 37.83 | 0.01003 | 0.09 | 0
PERIMETER_MID_ZN_2 | 8762.98 | 8762.98 | 66.76 | 0.647 | 0.647 | SUMMERDESIGNDAY | 2021-07-21 09:00 | 24 | 24 | 0.00867 | 27 | 0.00718 | 0.057 | 0
PERIMETER_MID_ZN_1 | 9102.25 | 9102.25 | 43.9 | 0.672 | 0.672 | SUMMERDESIGNDAY | 2021-07-21 14:00 | 24 | 24 | 0.00877 | 36 | 0.00904 | 0.09 | 0
PERIMETER_BOT_ZN_4 | 8472.57 | 8472.57 | 64.55 | 0.626 | 0.626 | SUMMERDESIGNDAY | 2021-07-29 17:20 | 24 | 24 | 0.00863 | 37 | 0.00929 | 0.057 | 0
PERIMETER_BOT_ZN_3 | 5849.04 | 5849.04 | 28.21 | 0.432 | 0.432 | SUMMERDESIGNDAY | 2021-07-21 16:00 | 24 | 24 | 0.00893 | 38 | 0.01012 | 0.09 | 0
PERIMETER_BOT_ZN_2 | 6583.05 | 6583.05 | 50.15 | 0.486 | 0.486 | SUMMERDESIGNDAY | 2021-07-21 09:20 | 24 | 24 | 0.00872 | 27.67 | 0.00739 | 0.057 | 0
PERIMETER_BOT_ZN_1 | 16711.96 | 16711.96 | 80.6 | 1.234 | 1.234 | SUMMERDESIGNDAY | 2021-07-28 18:00 | 24 | 23.99 | 0.00924 | 39 | 0.01026 | 0.09 | 0
CORE_TOP | 27746.41 | 27746.41 | 28.21 | 2.049 | 2.049 | SUMMERDESIGNDAY | 2021-07-29 16:50 | 24 | 24 | 0.00891 | 37 | 0.00962 | 0.425 | 0
CORE_MID | 20027.1 | 20027.1 | 20.36 | 1.479 | 1.479 | SUMMERDESIGNDAY | 2021-07-21 17:00 | 24 | 24 | 0.00907 | 34 | 0.00948 | 0.425 | 0
CORE_BOTTOM | 30007.34 | 30007.34 | 30.51 | 2.215 | 2.215 | SUMMERDESIGNDAY | 2021-07-21 09:00 | 24 | 24 | 0.00885 | 27 | 0.00718 | 0.425 | 0

## Peak sensible heating
| Calculated Design Load [W] | User Design Load [W] | User Design Load per Area [W/m2] | Calculated Design Air Flow [m3/s] | User Design Air Flow [m3/s] | Design Day Name | Date/Time Of Peak {TIMESTAMP} | Thermostat Setpoint Temperature at Peak Load [C] | Indoor Temperature at Peak Load [C] | Indoor Humidity Ratio at Peak Load [kgWater/kgAir] | Outdoor Temperature at Peak Load [C] | Outdoor Humidity Ratio at Peak Load [kgWater/kgAir] | Minimum Outdoor Air Flow Rate [m3/s] | Heat Gain Rate from DOAS [W]
CORE_BOTTOM | 0 | 0 | 0 | 0 | 0.425 | WINTERDESIGNDAY |  | 0 | 21 | 0.008 | -8 | 0.00162 | 0.425 | 0
CORE_MID | 5269.1 | 5269.1 | 5.36 | 0.227 | 0.425 | WINTERDESIGNDAY | 2021-12-28 06:00 | 21 | 21 | 0.01199 | -2 | 0.00274 | 0.425 | 0
CORE_TOP | 29063.36 | 29063.36 | 29.55 | 1.213 | 1.213 | WINTERDESIGNDAY | 2021-12-28 06:00 | 21 | 21 | 0.00949 | -2 | 0.00274 | 0.425 | 0
PERIMETER_TOP_ZN_3 | 12104.37 | 12104.37 | 58.38 | 0.508 | 0.508 | WINTERDESIGNDAY | 2021-12-28 06:00 | 21 | 21 | 0.0076 | -2 | 0.00274 | 0.09 | 0
PERIMETER_TOP_ZN_2 | 7982.2 | 7982.2 | 60.81 | 0.336 | 0.336 | WINTERDESIGNDAY | 2021-12-28 06:00 | 21 | 21 | 0.00761 | -2 | 0.00274 | 0.057 | 0
PERIMETER_TOP_ZN_1 | 12157.58 | 12157.58 | 58.64 | 0.511 | 0.511 | WINTERDESIGNDAY | 2021-12-28 06:00 | 21 | 21 | 0.00759 | -2 | 0.00274 | 0.09 | 0
PERIMETER_TOP_ZN_4 | 7938.14 | 7938.14 | 60.48 | 0.334 | 0.334 | WINTERDESIGNDAY | 2021-12-28 06:00 | 21 | 21 | 0.00761 | -2 | 0.00274 | 0.057 | 0
PERIMETER_BOT_ZN_3 | 5663.89 | 5663.89 | 27.32 | 0.239 | 0.239 | WINTERDESIGNDAY | 2021-12-28 06:00 | 21 | 20.99 | 0.00598 | -2 | 0.00274 | 0.09 | 0
PERIMETER_BOT_ZN_2 | 3933.85 | 3933.85 | 29.97 | 0.166 | 0.166 | WINTERDESIGNDAY | 2021-12-28 06:00 | 21 | 20.99 | 0.00613 | -2 | 0.00274 | 0.057 | 0
PERIMETER_BOT_ZN_1 | 23257.08 | 23257.08 | 112.17 | 1.012 | 1.012 | WINTERDESIGNDAY | 2021-12-24 08:00 | 21 | 20.98 | 0.00563 | -5 | 0.00226 | 0.09 | 0
PERIMETER_BOT_ZN_4 | 3862.29 | 3862.29 | 29.43 | 0.163 | 0.163 | WINTERDESIGNDAY | 2021-12-28 06:00 | 21 | 20.99 | 0.0061 | -2 | 0.00274 | 0.057 | 0
PERIMETER_MID_ZN_3 | 7742.6 | 7742.6 | 37.34 | 0.324 | 0.324 | WINTERDESIGNDAY | 2021-12-28 06:00 | 21 | 20.99 | 0.00647 | -2 | 0.00274 | 0.09 | 0
PERIMETER_MID_ZN_2 | 5296.66 | 5296.66 | 40.35 | 0.222 | 0.222 | WINTERDESIGNDAY | 2021-12-28 06:00 | 21 | 20.99 | 0.00659 | -2 | 0.00274 | 0.057 | 0
PERIMETER_MID_ZN_1 | 7605.34 | 7605.34 | 36.68 | 0.319 | 0.319 | WINTERDESIGNDAY | 2021-12-28 06:00 | 21 | 20.99 | 0.00644 | -2 | 0.00274 | 0.09 | 0
PERIMETER_MID_ZN_4 | 5223.33 | 5223.33 | 39.8 | 0.219 | 0.219 | WINTERDESIGNDAY | 2021-12-28 06:00 | 21 | 20.99 | 0.00657 | -2 | 0.00274 | 0.057 | 0
Max value | 29063.36 | 29063.36 | 112.17 | 1.213 | 1.213 | 0 | 44558.25 | 21 | 21 | 0.01199 | -2 | 0.00274 | 0.425 | 0